To:                     NAESB Office, WEQ Executive Committee Chairs

From:                 Kathy York, WEQ BPS Co-Chair

Subject:             Minor Correction:   WEQ-006, Version 0

Manual Time Error Correction

Date:                 August 22, 2006

At the August 21, 2006 meeting, the Business Practice Subcommittee determined that the two minor modifications needed to fulfill Request R06010 should have been performed during the original drafting of standard WEQ-006.  The Western Interconnection at the time of the drafting was already using a 5 second interval for initiation of corrections rather than the 2 second interval that we listed in the standards.  In addition, they never prescribed to the NERC limitation as specified for the Eastern Correction for not allowing fast time error corrections during the hours of 0400-1100 Central Time, as specified in WEQ-006-4.  The BPS unanimously voted to make these minor modifications.

The following minor corrections are highlighted below:

WEQ 006-4:

Time Error Initiation.  Time error corrections shall start and end on the hour or half-hour, and notice shall be given at least one hour before the time error correction is to start or stop.  Time Error corrections shall last at least one hour, unless terminated by a Reliability Coordinator.  Time Error corrections for fast time shall not be initiated between 0400-1100 Central Time except for in the Western Interconnection.  All Balancing Authorities within an Interconnection shall make all Time Error corrections directed by the Interconnection Time Monitor for its Interconnection.  All Balancing Authorities within an Interconnection shall make Time Error Corrections at the same rate.

WEQ 006 - 5

Interconnection time monitoring.  Each Interconnection Time Monitor shall monitor time error and shall initiate or terminate corrective action orders according to the following table:

|  | Initiation |  |  | Termination |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Time (seconds) | East | West | ERCOT | East | West | ERCOT |
| Slow | -10 | -5 | -3 | -6 | +/-0.5 | +/-0.5 |
| Fast | +10 | +5 | +3 | +6 | +/-0.5 | +/-0.5 |