## NAESBPAP10CommentSheet
C# | Company | Category | Cite | Suggested Change
1 | Aclara PLS | Technical | Fig 2 | Please define what is meant by "OverallConsumption" in the UsageSummary Class. 61968-9 Annex C enumerates and defines a number of important flow directions: "Net," "Total," "Forward," and "Reverse." Is it possibly one of these? Please also define what is meant by "NetConsumption" if "net" is not a flow direction. Otherwise, recommend deleting the "OverallConsumption" element. This is not the complete solution however as it may be impossible for the equipment to know if the meter is detented or not. What if it is not "net" metering that is occuring here but something else? You may be better off by just reporting a rather generic "consumption" with it understood to be either "forward," "net," or "total." Every element in the UsageSummary and PowerQualitySummary needs to be formally defined or there will be misunderstandings between the implementers of the different components.
2 | Aclara PLS | Technical | Fig 2. | How will enumeration schemes be identified? Even within a given scheme it is possible for it to evolve over time and gain or lose enumerations. How will two devices know if they both agree on the definitions? Suggest adding a naming authority element to the schema.
3 | Aclara PLS | Technical | Figs 1 and 2, Req18.4.1.18-19 | Quite a few of the classes support an "ID" element. In each case, please define how the ID is used and where it comes from. Is support for different naming authorities required? For example who says the meter number is what it is? Different systems identify it differently. How is the ReadingType ID defined? Recommend use of IEC 61968-9 Annex C. There should perhaps be an element to define the naming authority and/or version number of the scheme used. The NAESB std itself should have a revision number assigned to it, with the first revision being "1.0".
4 | Aclara PLS | Technical | Req 18.4.1.11 | The 4 flow directions defined by 61968-9 should be supported: Forward, Reverse, Net, and Total.
5 | Aclara PLS | Technical | Req 18.4.1.12 | I'm not aware of any new meter in North America supporting Q power. It may be possible to drop support for the Q power UOMs.
6 | Aclara PLS | Technical | Req 18.4.2.11.6 | I've found that prepackaged reports (such as the Usage Summary proposed in Fig 2) tend to have a rather limited shelf life. How will version control be performed? What if next year the summary report needs to contain something else? What if a developer adds to the model or doesn't support every element in a given report? How will two devices know that they are working with compatible versions? Suggest adding a version number element to the schema.
7 | Aclara PLS | Editorial | Req.18.4 and 18.4.2.11.12 | We're happy to see an effort being made to leverage the IEC CIM, and in particular an acknowlegement of IEC 61968 Part 9. In looking at the proposed schemas in Figures 1 and 2, it is very difficult to tell which elements are drawn from the CIM and which are proposed changes. I suggest that proposed extensions to the CIM be identified by a different color, or "namespace," or some other means.
8 | Aclara PLS | Editorial | Req.18.4 and 18.4.2.11.12 | The statement that "A MeterReading has a ReadingType which describes the nature of the measurement including its unit of measure,…" has a typo (in red).
9 | Aclara PLS | Technical | Req.18.4.1.19 | There are a number of UOMs which need clarification. For example is the "3" in "m3" a superscript?
10 | Aclara PLS | Technical | Req.18.4.1.19 | There appears to be duplicate UOMs: "Hz" is by definition equal to "s-1" (assuming the "-1" to be a superscript) and likewise "Hz-1" = "s". Recommend keeping "Hz" for frequency and "seconds" for time, and eliminating the other two.
11 | Aclara PLS | Technical | Req.18.4.1.19 | How is "pct" intended to be used as a unit of measure? Is it possibly instead a multiplier? Recommend moving "pct" and "ppm" to the multiplier class.
12 | Aclara PLS | Technical | Req.18.4.1.19 | It is quite likely that the standard, as used in North America, will require support for metrics such as cubic feet and other non-SI units of measure. Implementers know that any conversion from one UOM to another UOM results in roundoff errors. Recommend support of UOMs which tariffs are written to. If this isn't desirable, then one might go so far as to say that energy should be measured in Joules rather than kWh or BTU. This would put gas and electric meters into a common UOM. The customer however is unlikely to understand the intermediate UOM. Displays will have to convert back to the originally metered UOM, and then limit the resolution of the display to something less that what the worst meter is capable of in terms of accuracy and resolution.
13 | Aclara PLS | Technical | Req.18.4.1.19 | Implementers know that any conversion from one UOM to another UOM results in roundoff errors. Sometimes this is unavoidable. Since many of these values are billing determinants, and there are quite a few rules around how billing determinants can be rounded up or down, the conversion is not necessarily bidirectionally equivalent. It is very unlikely that the field equipment will be sophisticated enough to apply the regulatory rules correctly. Furthermore, the conversion of UOMs for a usage quantity can create a cumulative roundoff error. Load-profile interval data can create a situation where roundoff error can accumulate to significant amounts. Recommend a prominant disclaimer that says that all values are approximate.
14 | Aclara PLS | Technical | Req.18.4.1.19 | Additional work still needs to be done to reconcile the various units of measure from the different source materials into a common information model. Suggest the work being done in PAP06 and PAP14 be leveraged where possible to provide a semantic mapping.