1.  RECOMMENDED ACTION:	EFFECT OF EC VOTE TO ACCEPT RECOMMENDED ACTION:

| x | Accept as requested | x | Change to Existing Practice |
| --- | --- | --- | --- |
|  | Accept as modified below |  | Status Quo |
|  | Decline |  |  |

2.  TYPE OF DEVELOPMENT/MAINTENANCE

| Per Request: |  | Per Recommendation: |  |
| --- | --- | --- | --- |
| x | Initiation | x | Initiation |
|  | Modification |  | Modification |
|  | Interpretation |  | Interpretation |
|  | Withdrawal |  | Withdrawal |
| x | Principle | x | Principle |
| x | Definition | x | Definition |
| x | Business Practice Standard | x | Business Practice Standard |
| x | Document | x | Document |
| x | Data Element | x | Data Element |
| x | Code Value | x | Code Value |
|  | X12 Implementation Guide |  | X12 Implementation Guide |
| x | Business Process Documentation | x | Business Process Documentation |

3.  RECOMMENDATION

SUMMARY:

The recommended Business Practice Standards support the measurement and verification characteristics of Energy Efficiency products and services administered for application in the wholesale market and may be the subject of individual tariffs filed with and approved by the Federal Energy Regulatory Commission.

Recommended Standards:

DISCLAIMER:  This document contains draft information on standards for wholesale electricity Energy Efficeincy products and services in markets administered by Independent System Operators and Regional Transmission Organizations (hereinafter referred to as “System Operator”).  The information contained within this document is not intended to replace applicable Governing Documents for wholesale Energy Efficiency, and in the event of a conflict, the latter documents shall have precedence.

- Contact information:  Eric Winkler, Ph.D., ISO New England, 413-540-4513, ewinkler@iso-ne.com

WEQ-020  Business Practices Standards for Measurement and Verification of Energy Efficiency Products - Please see attached documentation.

WEQ.000

New Abbreviations/Acronyms and Defined Terms to be added to WEQ-000 in support of 2010 WEQ AP Items 4(g)

WEQ.000-1	ABBREVIATIONS AND ACRONYMS

| Abbreviation / Acronym | Meaning |
| --- | --- |
| ANSI | American National Standard Institute |
| ASHREA | American Society of Heating, Refrigeration and Air Conditioning Engineers |
| c.v. | Coefficient of Variation |
| EERP | Energy Efficiency Resource Provider |
| FEMP | Federal Energy Management Program (US) |
| HVAC | Heating, ventilating, and air conditioning |
| IEEE | Institute of Electrical and Electronics Engineers |
| IPMVP | International Performance Measurement and Verification Protocol |
| kHz | Kilohertz |
| M&V | Measurement and Verification |
| RMS | Root-Mean Square |
| VEE | Validation Editing and Estimation |

WEQ.000-2	DEFINITION OF TERMS

| Term | Definition |
| --- | --- |
| Demand Reduction Value | The measurement of reduced electricity usage by a Demand Resource during a Demand Response Event or Energy Efficiency performance hours expressed in MW. |
| Energy Efficiency | Installed measures on Retail Customer facilities that achieve a permanent reduction in electric energy usage while maintaining a comparable quality of service. |
| Energy Efficiency Baseline | Energy usage that would have occurred without implementation of the subject measure or project |
| Energy Efficiency Capacity Resource | A type of Demand Resource used in capacity markets in which demand is reduced over a defined period of time measured in MW. |
| Energy Efficiency Resource Provider | An entity that is responsible for delivering Energy Efficiency. |
| Measurement and Verification | The process of determining reductions in usage and/or demand resulting from Demand Response or Energy Efficiency. |

- Measurement and Verification of Energy Efficiency Products

  - Introduction and Principles

    - Introduction and Principles

Energy Efficiency Resource Providers (“EERP”) that offer Energy Efficiency resources into wholesale electricity markets must provide consistent and reliable evidence of reductions in electrical usage for qualification and performance.  Methodologies for Measurement and Verification (“M&V”) of demand reduction shall be established by the System Operator and compliance with said requirements shall be the responsibility of the EERP. Compliance with the standards are intended to ensure that Energy Efficiency Resources are qualified for participation in the market and the Demand Reduction Values, in performance reporting, accurately reflect the demand reduction delivered to the electrical system.

A Business Practice Standard for M&V of Energy Efficiency has the potential to broaden implementation and acceptance of energy reduction measures and practices.  The standards are not designed to establish or support any regulatory policy.

  - Applicability

      - This document contains information on standards for M&V of wholesale electricity Energy Efficiency products and services in markets administered by ISOs and RTOs (hereinafter referred to as “System Operator”).  The information contained within this standard is not intended to replace applicable Governing Documents applicable to wholesale Energy Efficiency.  In the event of a conflict between these standards with the Governing Documents, the Governing Documents shall have precedence over these standards.

      - These standards establish Energy Efficiency M&V criteria.  They do not establish requirements related to the compensation, design, operation, or use of Energy Efficiency services.  These standards do not require the System Operator  to offer services including Energy Efficiency.  Terms that are capitalized in these standards have the meanings ascribed to them in the Definitions of Terms section of the WEQ-000 Business Practice Standards.

      - These Standards include the requirements on EERPs for the M&V of Energy Efficiency offered into wholesale markets.  References not limited to submission of materials, use of equipment,  measurement, sampling and calculations refer to materials submitted to the System Operator by the EERPs and actions taken by the EERP.

  - Business Practice Standards

    - Energy Efficiency Use Criteria in Wholesale Markets

The following criteria comprise elements of how Energy Efficiency may participate in wholesale markets but are not requirements for M&V of Energy Efficiency products in wholesale markets.  Detailed criteria in standards WEQ.0203.3. to WEQ.0203.12 shall constitute the required elements of M&V for EERPs participating in wholesale electric markets.

      - Installation and Eligibility 
Verified permanent load reduction behind the distribution meter resulting from installation of Energy Efficiency equipment, processes, or systems that exceed Energy Efficiency codes and standards at the time of commitment, installation or permanent load shifting.

      - Modeling Energy Efficiency 
An Energy Efficiency Capacity Resource may be modeled in the system equivalent to other supply side resources in accordance with the applicable Governing Documents.

      - Increase in Energy Efficiency Value 
Energy Efficiency Capacity Resource may be augmented via incremental or reconfiguration auctions, provided such resource is qualified in advance of the applicable auction in accordance with the applicable Governing Documents.

      - Early Completion
Energy Efficiency Capacity Resource that is deliverable in a period in advance of the commitment period, for which it originally cleared, may participate in prior commitment periods subject to qualification requirements specified in the applicable Governing Documents.

    - General Measurement and Verification Plan Requirements 
 
A document that defines specific M&V methods for verifying the Demand Reduction Value is required of EERPs for qualification and participation in the program, market, product class or auction.  The following general elements of M&V plans are not required or exhaustive.  Detailed criteria in standards WEQ.0203.3 to WEQ.0203.12 shall constitute the required elements of an M&V plan as specified in the regional Governing Documents.

      - Project Description
Plan should include a project description, not limited to: a general description of the project location, facility types, measure types, estimated Demand Reduction Value, estimated cost of project (capital, operation and M&V) and savings.

      - Schedule
Plan should include project schedule describes the timeline of a project build out for establishing qualification eligibility.  Plans shall specify a schedule of M&V activity during project buildout and during delivery period.

      - Measure Description
Plan should include measure level characteristics, including but not limited to: Demand Reduction Values based on metering, engineering estimates, or model simulation.

      - Equipment/Process Specification and Documentation
Plan should include a detailed description of existing and new equipment and process characteristics sufficient to establish Energy Efficiency Baseline calculations.

      - Measurement and Verification Approach
Plan should include justification of appropriate measurement methodology, not limited to the four International Performance M&V Protocol (IPMVP) methodologies at the measure level.

      - Methodological Assumptions

Plan should include a detailed description of underlying assumptions for Energy Efficiency Baseline and post installation energy use.

      - M&V Activities: Energy Efficiency Baseline Period
Plan should include a description of the period of time under which the Energy Efficiency Baseline will be quantified.

      - M&V Activities: Post Installation Period

Plan should include a description of activities conducted post installation to document actual Demand Reduction Values.

      - Calculation and Adjustments
Plan should include a detailed description of calculations used to establish Energy Efficiency Baseline and actual Demand Reduction Value.

      - Metering Plan
Plan should include a detailed description of meter management, not limited to maintenance, meter data collection and processing.

      - Updated M&V Plan Components
Plan should include a description of process by which M&V plan updates are made and documented.

    - Post installation M&V Report Components

      - Initial Post-Installation M&V Report: 
During the course of project buildout, a post-installation report shall be submitted by the EERP to the ISO/RTO to document the verified reductions resulting from installed measures. The report shall be required at least annually.

      - Updated Post-Installation M&V Report
An updated performance report shall be submitted by the EERP to the ISO/RTO to document achieved reductions for the purposes of establishing reduction values carried into subsequent delivery periods.  The report shall be required at least annually

.

    - Performance Reporting

      - Minimum Requirements
Performance reports shall be submitted by the EERP to the ISO/RTO to document achieved reductions during the delivery period.  Report shall be required at least annually.

    - M&V Supporting Documents

      - Minimum Requirements
All reports, studies, specifications and other documents referenced by the EERP in the M&V Plan shall be current and applicable to the measures.

    - M&V Methodologies

      - Acceptable Methodologies
 Measurement and Verification methodologies used by the EERP shall be appropriate to the measure type and sensitivity requirements of the measurement techniques.  Acceptable methods shall include:

        - IPMVP Option A: Partially Measured Retrofit Isolation/Stipulated Measurement. 

IPMVP Option A may involve an equipment specific retrofit or replacement, new installation or a system level Measurement and Verification assessment. The approach is intended for measures where either performance factors (such as lighting wattage) or operational factors (such as operating hours) can be measured on a spot or short-term basis during baseline establishment and post-installation periods, or for measures for which a measured proxy variable can, in combination with well-established algorithms and/or stipulated factors, can provide an accurate estimate of the Demand Reduction Value.

        - IPMVP Option B: Retrofit Isolation/Metered Equipment.

IPMVP Option B involves a retrofit or system-level Measurement and Verification assessment. The approach is intended for retrofits with performance factors and operational factors that can be measured at the component or system level using interval electrical demand meters installed on the affected end-use.

        - IPMVP Option C: Whole facility/Regression.

IPMVP Option C estimates Demand Reduction Values by analyzing the overall energy use in a facility and identifying the impact of the implemented measure on the total building or facility energy use patterns. The evaluation of whole-building or facility level metered data is completed using techniques ranging from simple billing comparison to multivariate regression analysis.

        - IPMVP Option D: Calibrated Simulation.

IPMVP Option D involves calibrated computer simulation models of component or whole building demand and energy usage to determine measure demand and energy savings.  Engineering simulation models (such as DOE-2) can model both residential buildings (homes, apartments and condominiums) as well as more complex commercial buildings.  Operational simulations can be used for industrial processes that take into account the specifics of the process addressed by the energy efficiency actions.  Both engineering and operational simulations are made more powerful by calibrating these methods to actual MW and MWh data from the site or process being examined, even if these data are available for a monitoring period shorter than or different from the required performance hours.  Short-term metering and monitoring are methods that produce data that can be used to adjust engineering simulations.  This approach is generally termed "calibrated engineering simulations."  Linking simulation inputs to baseline and post-installation conditions completes the calibration.  Characterizing baseline and post-installation conditions may involve metering performance and operating factors both before and after the retrofit.  Long-term whole-building energy use data may be used to calibrate the simulations.

        - Alternative Acceptable M&V Methodologies.  

The EERP may propose alternative methodologies not listed in the Section above.  EERPs proposing alternative methodologies shall demonstrate that the alternative methodologies will be equivalent to one of the accepted methodologies described above, and demonstrate justifiable need for deviation from the acceptable methodologies described in the Section above based on unique Project requirements.

    - Energy Efficiency Baseline Conditions

      - Energy Efficiency Baseline Criteria for all Energy Efficiency
Energy Efficiency Baseline conditions used by the EERP shall reflect the conditions under which new energy efficient equipment or processes are installed to provide a service function.  The four conditions shall include:

        - Replacement of functional equipment still within its current useful life.

        - Replacement of functional equipment beyond its current useful life.

        - Unplanned replacement or failed equipment.

        - New construction.

      - The standard Energy Efficiency Baseline used by the EERP shall be the nameplate rating of the equipment meeting the level of efficiency required by applicable state code, federal product efficiency standard, or standard practice, whichever is most stringent.  The standard Energy Efficiency Baseline is determined at the time of commitment in the case of forward commitment or at the time of installation as set forth in the Governing Documents.  The standard Energy Efficiency Baseline shall be applied to criteria 020.3.7.1.3, 020.3.7.1.4. The standard Energy Efficiency Baseline shall be applied to criteria 020.3.7.1.2, unless otherwise specified by the Governing Documents.

      - The current load Energy Efficiency Baseline used by the EERP shall be the existing load of operating equipment across the performance hours.  The current load Energy Efficiency Baseline is determined at the time of commitment in the case of forward commitment or at the time of installation as set forth in the Governing Documents.  Use of current load Energy Efficiency Baseline shall be applied to criteria 020.3.7.1.1. Use of current load Energy Efficiency Baseline may be applied to criteria 020.3.7.1.2, if specified by the Governing Documents.

    - Statistical Significance

      - General Requirements
M&V of Energy Efficiency may include measurement methodologies requiring statistical estimation techniques for Demand Reduction Values.  In the event that statistical methods are required, the following requirements for statistical significance shall be met.

      - Sample Size
Specification for statistical error and precision in sampling.  The use of a bi-directional t-test (two-tailed) may be required of the EERP where performance reporting may result in both performance bonuses and or penalties.  Sample Error and Precision used by the EERP shall be 80/10 using a two-tailed test or 90/10 using a one-tailed test subject to the Governing Documents. Compliance with this criterion shall be applicable to the overall  Demand Reduction Value of the Energy Efficiency Capacity Resource.

      - Sample Size Calculation
The sample size used by the EERP requires the use of a population coefficient of variation (c.v.) which may not be known at the time of sample design.  The sample size may be established using an estimate of the c.v. based on the following criteria.  The estimated c.v. for homogeneous populations used by the EERP shall be 0.5 and 1.0 for heterogeneous populations.

      - Sample Size Recalibration
Population sampling error and precision used by the EERP shall be recalibrated using a measured c.v..  The sample c.v. used by the EERP shall be calculated from the measured sample population and applied to the reported estimate of sampling error and precision.

      - Sampling Over Zones
Sampling used by the EERP over heterogeneous zones shall control for bias and meet the overall error and precision requirements.

      - Sample Bias Control
Types of potential sampling bias control to be used by the EERP include, but are not limited to: (a) construct validity; (b) sampling frame versus population; (c) selection bias (for a sample and for a census attempt where not all sites within the census received usable data); (d) non-response bias; (e) error in measuring variables; (f) sample homogeneity relative to project (external validity); (g) outlier data points; and (h) missing data.  Sampling plans submitted by the EERP shall demonstrate and document that population sampling bias is minimized.

    - Nominated Energy Efficiency Value Calculations/Demand Reduction Value Calculations

      - Nominated Energy Efficiency Values 
Calculation of Demand Reduction Values for equipment, measures and practices, including weather sensitive loads, may include estimated modifiers or variables.  

Estimated modifiers and variables used by the EERP in the calculation of the Demand Reduction Value shall include but are not limited to: coincidence factor, realization rate, equipment failure rate, and normalization method for weather sensitive loads.

      - Reduction in the Final Nominated Value
If the reported Demand Reduction Value does not meet the precision standard, the final performance value may be reduced.

Governing Documents shall dictate the calculation of further reductions to reported Demand Reduction Values.

    - Measurement and Monitoring

      - Measurement and Monitoring Requirements 
Measurement and monitoring involve the collection of data of various types from equipment, measures and practices.   Monitoring parameters and variables shall be used in the calculation of the Demand Reduction Value.

The EERP shall document all monitoring parameters and variables measured for use in calculation of the Demand Reduction Value.

All monitoring parameters used in the calculation of the Demand Reduction Value shall be applicable to the category of equipment, measure or practice, including but not limited to: heating ventilating and air conditioning (HVAC) equipment, HVAC controls, building envelopes, interior/exterior lighting, major electric consuming equipment and weather sensitive loads

      - Monitoring Frequency and Duration 
Monitoring frequency and duration of sampling must be controlled by the EERP so as to reduce measurement error.

The frequency and duration of measurement and monitoring used by the EERP shall be sufficient to ensure accurate representation of the Demand Reduction Value during the performance hours or minimum reporting interval, whichever is less, consistent with statistical significance requirements in section WEQ.0203.8.

    - Measurement Equipment Specification

      - Measurement Equipment Requirements
Measurement equipment devices used by the EERP shall have the following technical requirements:

        - All solid-state measurement, monitoring and data recording equipment shall meet or exceed the relevant standards set by the American National Standard Institute (“ANSI”) or equivalent standard for the equipment.

        - Measurement, monitoring and data recording equipment that is directly measuring watt-hour, volt-hour, volt-ampere-hours, reactive volt-ampere-hour, and the associated demand components should conform to ANSI or equivalent standards for the equipment.

        - Instruments or transducers for the analog or digital measurement of volt, volts-squared, amperes, amperes-squared, phase angle, volt-amperes, watts, and reactive volt-amperes should conform to ANSI or equivalent standards for the equipment.

        - Data recorders that are recording pulses from measurement and monitoring devices shall use a pulse rate within the resolution capabilities of the recorder.

        - All measurement, monitoring and data recording equipment installed on electric circuits with significant harmonics shall meet the relevant standards provided by the Institute of Electrical and Electronics Engineers (“IEEE”).

        - Any measurement or monitoring equipment that directly measures electrical demand in MW shall be a true Root-Mean Square (“RMS”) measurement device with an accuracy of no less than ±2%.

        - Any measurement or monitoring equipment that directly measures electrical demand from three-phase devices shall be installed such that measurements are taken on all three-phases to account for any phase imbalance or an equivalent method that can measure electrical demand using two phases.

        - Any measurement or monitoring equipment that directly measures electrical demand on circuits with significant harmonics shall have a digital sampling rate of at least 2.6 kilohertz (kHz) as defined in the relevant IEEE Standards.

        - Any measurement or monitoring equipment for proxy variables that do not directly measure electrical demand, including but not limited to voltage, current, temperature, flow rates and operating hours, shall have an accuracy of ± 2%, unless otherwise provided in the Governing Documents.

        - Any measurement or monitoring equipment of current amps and nominal voltage used to calculate electrical demand shall include the power factor of the end-uses in the demand MW calculations.

        - Data recorders shall be synchronized in time, within an accuracy of ± 2 minutes per month, with the National Institute of Standards and Technology (“NIST”).

        - All measurement, monitoring and data recording equipment shall be calibrated by the EERP, independent calibration contractor, or designee, to meet or exceed the IPMVP, the US DOE Federal Energy Management Program (“FEMP”) M&V guidelines, applicable American Society of Heating, Refrigeration and Air Conditioning Engineers (“ASHRAE”) standards, NIST, or equivalent standard for the equipment.

        - All measurement, monitoring and data logging equipment shall be maintained in such a way as to meet or exceed industry and manufacturer maintenance standards.

        - Documentation on all measurement, monitoring and data recording equipment maintenance and calibration activities shall be maintained in accordance with applicable regional record retention policies as specified in Governing Documents.

        - Interval metering devices that sample continuously and integrate values shall collect data at a frequency of one hour or less.  Interval meter devices that sample using snapshots shall collect electricity usage data at a frequency of 15 minutes or less.

    - Data Validation

      - All measured data used in the Demand Reduction Value calculations shall be validated using standard Validation, Editing, and Estimation (VEE) procedures.  For Projects involving an individual facility or energy consuming equipment, the following validation checks on any interval data from an individual facility shall be made by the EERP:

        - Time Check:  validate that the measurement devices time clock is within ± two minutes of the true time as defined by NIST.

        - Sum Check:  validate that the difference between the sum of the values recorded over the intervals and the value recorded by the meter over the same time-period is within ± 2%. This check may be performed on either usage or pulse data, provided the data scaling is consistent throughout the period.

        - High/Low Check: establish minimum and maximum expected values for each Demand Asset, facility, or measure.  The minimum and maximum values shall be based on equipment ratings or historical equipment and/or facility usage data.  All interval data that is greater than the maximum expected value or less than the minimum expected value shall be identified. Any such interval data shall be deemed to fail validation.

        - Zero Value Check:  identify any interval data with a value equal to zero.  Verification of whether the zero value is the correct value for that interval shall be made.  If it is determined that the zero value is incorrect, substitution of a corrected or estimated non-zero value for the zero value may be allowed.  Under no circumstances shall a zero value be substituted for missing interval data.

        - The EERP shall identify all estimated data used in the Demand Reduction Value calculations, as well as the methodology used to develop the estimate.

        - The EERP shall classify all data that have passed validation and used in the Demand Reduction Value calculations as either: (i) actual data, (ii) estimated data or (iii) missing data.  The data classification shall be stored along with the data values in the data retention and management system prescribed by the System Operator.

4.  SUPPORTING DOCUMENTATION

              - Description of Request:

WEQ 2010 Annual Plan Item 4 (d)

Develop business practice standards used to measure and verify reductions in energy and demand from energy efficiency in wholesale and retail markets.   This includes developing business practice standards to measure and verify energy reductions that are made to comply with a Renewable Portfolio Standard that included energy efficiency or a stand-alone Energy Efficiency Portfolio Standard.

              - Description of Recommendation:

The recommended Business Practice Standards support the measurement and verification characteristics of Energy Efficiency products and services administered for application in the wholesale market and may be the subject of individual tariffs filed with and approved by the Federal Energy Regulatory Commission.

              - Business Purpose:

              - Commentary/Rationale of Subcommittee(s)/Task Force(s):

Standards for M&V of energy efficiency should consider a balance in rigor, which effects measurement investment cost.  M&V activities are commonly decided by the entity making the efficiency investment and are guided by the cost benefit, product specification and business model.  As such, methodologies for M&V have varying degrees of rigor or quantitative precision and accuracy.   A standard that can result in accurate valuation of implemented measures and practices, which is flexible, consistent, and cost effective, will be most useful to the industry and the public.  The standards reflecting the minimum requirement for M&V of Energy Efficiency should build on industry and public experience as well as accommodate evolutionary changes to the application of engineering, science and economics that are the basis of energy efficiency efforts.

“The International Performance Measurement and Verification Protocol (IPMVP) provides an overview of current best practice techniques available for verifying results of energy efficiency, water efficiency, and renewable energy projects in commercial and industrial facilities.”  Efficiency Valuation Organization, 2010. http://www.evo-world.org.  The IPMVP (EVO 10000 – 1:2010, © Efficiency Valuation Organization 2010), may be obtained from EVO-world.org and may be periodically updated.

M&V Guidelines: Measurement & Verification for Federal Energy Projects Version 3.0, US DOE Federal Energy Management Program, April 2008